## table
Location | Settings |  |  |  | Limits |  | Results from Field Tester |  |  | Notes | Analysis Results
| DR | SF | TX Power |  | Min. Sampling Rate | min SNR for SF | RSSI | SNR | Gateway Count | Obstacles, machinery, power lines etc. | SNR | Gateway Count | Recommendations (not yet finished work in progress)
| [-] | [-] | [-] | [dBm] | [h:min] | [dB] | [dBm] | [dB] | [-]
Office | 1 | 11 | 0 | 14 | 1h 16min | -17.5 | -118 | 2 | 1 |  |  | Add Gateway to be safe. | Try DR2/ SF10
added new Gateway gtw-02
Office | 1 | 11 | 0 | 14 | 1h 16min | -17.5 | -88 | 2 | 2 |  |  |  | Try DR2/ SF10

## metadata
DR | SF | Minimum SNR [dB] | Bitrate | Airtime | Min. Sampling Rate | Min. Sampling Rate
|  | [db] | [bps] | [ms/telegram] | [decimal hours] | [h:min]
5 | 7 | -7.5 | 5470 | 127.2395 | 0.10179 | 6min
4 | 8 | -10 | 3125 | 222.72 | 0.17818 | 11min
3 | 9 | -12.5 | 1760 | 395.4545 | 0.31636 | 19min
2 | 10 | -15 | 980 | 710.2041 | 0.56816 | 34min
1 | 11 | -17.5 | 440 | 1581.8182 | 1.2655 | 1h 16min
0 | 12 | -20 | 250 | 2784 | 2.2272 | 2h 14min
TX Power | dBm
7 | 7
6 | 8
5 | 9
4 | 10
3 | 11
2 | 12
1 | 13
0 | 14
Payload | 51 | bytes
Header | 36 | bytes
Duty Cycle | 0.1 | %
Max Airtime | 30 | s/day
RSSI Thresholds
[dBm] |  | [-]
-125 | < -125 | Limit | Unusable | Add an addintional Gateway
-115 | range -115 … -125 | Bad | Weak signal, only works at high SF | unreliable, needs higher SF or TX power or additional gateway
-100 | range -100 … -115 | Fair | Fair signal, maybe unreliable | Possibly unreliable, may need higher SF or TX power
-90 | range -90 … -100 | Good | Strong signal
> -90 | > -90 | Excellent | Very strong signal
SNR Thresholds
[dBm] | range | label
-15 | < -15 | Limit | Very noisy, SNR below limits for LoRa | Add an additional Gateways
-7 | range -7 … -15 | Bad | Very noisy, SNR below limits for LoRa | Add an additional Gateways
0 | range 0 … -7 | Fair | Acceptable, SF7 could have problems, less SF12 | Try with a lower SF, if required sampling rate does not allow it then add an additional Gateway
5 | range 5 … 0 | Good | clean signal
| > 5 | Excellent | Very clean signal